## Size
Component | Unit | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Total
PV panels | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind turbines | kW | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08 | 232.08
Battery bank | kWh | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06 | 176.06
Diesel Genset | kW | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69 | 366.69

## Cost
Cost item | Component | Scenario | Unit | Step 1 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 2 | Step 20 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Total
Net present cost | System | - | kUSD | [20 empty] | 1711.812 | bar: Step 1 to Step 9
Total Investment cost | System | - | kUSD | [20 empty] | 644.606 | bar: Step 1 to Step 9
Total fixed O&M cost | System | - | kUSD | [20 empty] | 78.58 | bar: Step 1 to Step 9
Total variable O&M cost | System | - | kUSD | [20 empty] | 988.628 | bar: Step 1 to Step 9
Salvage value | System | - | kUSD | [20 empty] | -0.002 | bar: Step 1 to Step 9
Levelized Cost of Energy | System | - | USD/kWh | [20 empty] | 0.3401 | bar: Step 1 to Step 9
Investment cost | PV panels | - | kUSD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind turbines | - | kUSD | 464.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464.166
| Battery bank | - | kUSD | 70.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.424
| Diesel Genset | - | kUSD | 110.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 110.016
Fixed cost | PV panels | - | kUSD | [20 empty] | 0 | bar: Step 1 to Step 9
| Wind turbines | - | kUSD | [20 empty] | 19.759 | bar: Step 1 to Step 9
| Battery bank | - | kUSD | [20 empty] | 1.408 | bar: Step 1 to Step 9
| Diesel Genset | - | kUSD | [20 empty] | 46.83 | bar: Step 1 to Step 9
Lost load cost | System | 1 | kUSD | [20 empty] | 0 | bar: Step 1 to Step 9
Replacement cost | Battery bank | 1 | kUSD | [20 empty] | 14.016 | bar: Step 1 to Step 9
Fuel cost | Diesel | 1 | kUSD | [20 empty] | 974.611 | bar: Step 1 to Step 9

## Yearly cash flows
| Fixed costs |  |  |  | Lost load cost | Replacement cost | Fuel cost
Component | PV panels | Wind turbines | Battery bank | Diesel Genset | System | Battery bank | Diesel
Scenario | - | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.37
Year 2 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.43
Year 3 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.44
Year 4 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.45
Year 5 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.46
Year 6 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.47
Year 7 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.48
Year 8 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.48
Year 9 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.49
Year 10 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.5
Year 11 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.51
Year 12 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.52
Year 13 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.53
Year 14 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.55
Year 15 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.56
Year 16 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.57
Year 17 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.58
Year 18 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.59
Year 19 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.6
Year 20 | 0 | 2.32 | 1.41 | 5.5 | 0 | 1.65 | 114.61

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage
| % | % | % | %
Year 1 | 51.93 | 56.24 | 15.37 | 5.36
Year 2 | 51.96 | 56.23 | 15.37 | 5.34
Year 3 | 51.96 | 56.22 | 15.36 | 5.34
Year 4 | 51.96 | 56.22 | 15.36 | 5.34
Year 5 | 51.96 | 56.22 | 15.36 | 5.34
Year 6 | 51.96 | 56.22 | 15.36 | 5.34
Year 7 | 51.96 | 56.22 | 15.35 | 5.34
Year 8 | 51.96 | 56.21 | 15.35 | 5.34
Year 9 | 51.96 | 56.21 | 15.35 | 5.34
Year 10 | 51.96 | 56.21 | 15.34 | 5.34
Year 11 | 51.96 | 56.21 | 15.34 | 5.34
Year 12 | 51.96 | 56.21 | 15.34 | 5.34
Year 13 | 51.96 | 56.2 | 15.33 | 5.34
Year 14 | 51.96 | 56.2 | 15.33 | 5.34
Year 15 | 51.96 | 56.2 | 15.33 | 5.34
Year 16 | 51.96 | 56.2 | 15.32 | 5.34
Year 17 | 51.97 | 56.19 | 15.32 | 5.34
Year 18 | 51.97 | 56.19 | 15.31 | 5.34
Year 19 | 51.97 | 56.19 | 15.31 | 5.34
Year 20 | 51.97 | 56.19 | 15.31 | 5.34